3.1 General questions

What extreme scenarios must be analysed before deciding if the connection of DER is permissible?

Testing according to DIN EN 50160:

Maximum load & minimum generation at all voltage levels

Minimum load 1)  & maximum generation at all voltage levels

1) Value for the load depends on the times, when maximum DER feed-in occurs (e.g. for PV between 10 am and 4 pm).

What tap-changer position (set-point value for voltage regulation on MV side) should be assumed for the HV/MV transformer depending on the scenario?

Maximum load & minimum generation at all voltage levels, minimum tapping (within control range) at HV / MV transformer

Minimum load 1) & maximum generation at all voltage levels, maximum tapping (within control range) at HV/MV transformer

What is the maximum permissible voltage rise (in % of nominal voltage) for the MV and LV level during normal operation? How does this threshold change during n-1 contingency conditions?

Testing according to technical connection rules during normal conditions:

MV level (bdew): voltage change when all DER are connected (compared to the case without any DER)

LV level (VDE AR 4100 and 4105): voltage change when all DER are connected

During normal operation (continuous voltage fluctuation)

Maximum voltage deviation at PCC (Point of Common Coupling)

LV: -5% to +10%

MV: -5% to +5% Defined for 95% of the time, measured over one week

During fault conditions (n-1 case, single outage):

LV: -8% to +10%

MV: -10% to +10%

After reactive actions (e.g., stepping of on-load tap-changer):

MV: -8% to +8%

What is the maximum permissible line loading under normal conditions for the MV and LV level?

Testing according to technical connection rules:

Maximum load & minimum generation at all voltage levels, minimum tapping (within control range) at HV / MV transformer

Minimum load 1) & maximum generation at all voltage levels In both cases, minimum tapping at HV / MV transformer

1) Value for the load depends on the times, when maximum DER feed-in occurs (e.g. for PV between 10 am and 4 pm).

For the current limits, the maximum steady-state loading is limited to 100 % of the long-term assets capacity. Some DSOs make exceptions, e.g., allowing a temporarily loading of 130 % of maximum steady-state loading for MV/LV stations.

Based on the results for high load conditions, is the network n-1 secure? Which measures would you recommend for ensuring n-1 security?

For LV high load, low DER condition, it is not n-1 secure. We got line [9] as critical node.

Measures: Add a parallel line || Add parallel source feed in the system

Repeat the power flow calculation for light load, very high PV conditions. What difference do you notice?

More bus voltage increment because we have light load but more DER gen.

Extra DER gen. is feed to all grid systems (HV, MV, LV).

Compare the voltage drop / voltage rise with the permissible bandwidth. Is the network well designed?

During normal operation (continuous voltage fluctuation)

Maximum voltage deviation at PCC (Point of Common Coupling)

LV: -5% to +10%

MV: -5% to +5% Defined for 95% of the time, measured over one week .

The MV network is not well-defined while for high load low DER gen. we have from (Bus 3 – Bus 11)  – min bus voltage < 0.95 p.u. and for low load high DER gen. we have from (Bus 3 – Bus 11) – max bus voltage > 1.05 p.u.

The LV network is not well-defined while for high load low DER gen. we have from (Bus 6 – Bus 19)  – min bus voltage < 0.95 p.u.

Which annual consumptions is assumed for the H0 load profile? How do you scale the profile for different levels of consumption?

Scaling  - We divide all the load with the max load of all time.

Annual Consumption was assumed to be 1000KWh.

What is the morning and evening peak in consumption?

H0 load profile --- Morning peak --- > 173.1 W      Evening peak --- > 213.2

G0 load profile --- Morning peak --- > 200 W      Evening peak --- > 178.5

In which time of the year do you expect the peak household consumption? Is this the same for all countries, or rather specific to Germany?

Winter. No.

Time Series Analysis without DER:-

Weekday in Summer: Residential Case (H0)

maximum, mean, and minimum voltage of the buses at MV voltage level

maximum, mean, and minimum voltage of the buses at LV voltage level

Mean and maximum line loading over time

Sunday in fall/Spring: Residential Case (HO)

maximum, mean, and minimum voltage of the buses at MV voltage level

maximum, mean, and minimum voltage of the buses at LV voltage level

Mean and maximum line loading over time

Saturday in Winter: Residential Case (HO)

maximum, mean, and minimum voltage of the buses at MV voltage level

maximum, mean, and minimum voltage of the buses at LV voltage level

mean and maximum line loading over time

Weekday in Summer: Commercial Case (G0)

maximum, mean, and minimum voltage of the buses at MV voltage level

maximum, mean, and minimum voltage of the buses at LV voltage level

mean and maximum line loading over time

Sunday in Spring: Commercial Case (G0)

maximum, mean, and minimum voltage of the buses at MV voltage level

maximum, mean, and minimum voltage of the buses at LV voltage level

mean and maximum line loading over time

Saturday in Winter: Commercial Case (G0)

maximum, mean, and minimum voltage of the buses at MV voltage level

maximum, mean, and minimum voltage of the buses at LV voltage level

mean and maximum line loading over time

Time Series Analysis with DER only active power:-

Workday in Summer: Residential Case (H0)

maximum, mean, and minimum voltage of the buses at MV voltage level

maximum, mean, and minimum voltage of the buses at LV voltage level

the mean and maximum line loading over time

Workday in Summer: Commercial Case (G0)

maximum, mean, and minimum voltage of the buses at MV voltage level

maximum, mean, and minimum voltage of the buses at LV voltage level

the mean and maximum line loading over time

Sunday in Spring: Residential Case (H0)

maximum, mean, and minimum voltage of the buses at MV voltage level

maximum, mean, and minimum voltage of the buses at LV voltage level

the mean and maximum line loading over time

Sunday in Spring: Commercial Case (G0)

maximum, mean, and minimum voltage of the buses at MV voltage level

maximum, mean, and minimum voltage of the buses at LV voltage level

the mean and maximum line loading over time

Saturday in Winter: Residential Case (H0)

maximum, mean, and minimum voltage of the buses at MV voltage level

maximum, mean, and minimum voltage of the buses at LV voltage level

the mean and maximum line loading over time

Saturday in Winter: Commercial Case (G0)

maximum, mean, and minimum voltage of the buses at MV voltage level

maximum, mean, and minimum voltage of the buses at LV voltage level

the mean and maximum line loading over time

Compare the maximum voltage drop/rise in the MV and LV network as well as the maximum line loading to the results from section 3. Which approach (scenario-based or time series) yields more onerous results?

Since we did not use the time series analysis more onerous is scenario-based analysis. We found out that the values for bus voltages are exceeding the permissible limits in Scenario based analysis.

Exercise 5

| Network | Measurements |  | Scenario MV |  | Scenario LV |  | Scenario Combined | Time Series |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | High load, low DER gen. | Low load high DER gen. | High load, low DER gen. | Low load high DER gen. |  |  |
| MV | Bus Voltage | min | 0.902 | 1.02 |  |  | 0.902 |  |
|  |  | max | 1.03 | 1.06 |  |  | 1.06 |  |
|  |  | mean | 0.937 | 1.04 |  |  | 0.99 |  |
|  | Line Loading | max | 99.88 | 64.30 |  |  | 99.98 |  |
|  |  | mean | 27.44 | 17.58 |  |  | 22.51 |  |
| LV | Bus Voltage | min |  |  | 0.91 | 1.0 | 0.91 |  |
|  |  | max |  |  | 1.0 | 1.04 | 1.04 |  |
|  |  | mean |  |  | 0.94 | 1.02 | 0.98 |  |
|  | Line Loading | max |  |  | 32.52 | 22.53 | 32.52 |  |
|  |  | mean |  |  | 18.83 | 18.83 | 18.83 |  |